Please Note:

This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose. You agree that your use of the template is without any recourse whatsoever to PG&E, SCE, SDG&E, or their affiliates. The template is a draft, and anyone using this document should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ.

This document is the product of a collaborative effort between Peninsula Clean Energy, Silicon Valley Clean Energy, and the Local Energy Codes team.

Please contact the Codes and Standards Local Energy Codes Team at info@LocalEnergyCodes.com for additional information.

Message paid for by customers. This program is funded by California utility customers and administered by Pacific Gas and Electric Company, San Diego Gas & Electric Company (SDG&E®), and Southern California Edison Company under the auspices of the California Public Utilities Commission and in support of the California Energy Commission.

REACH CODE IMPLEMENTATION RESOURCES TEMPLATE

2025 NON-RESIDENTIAL ROOFTOP HVAC UNIT REPLACEMENT CHECKLIST

Version 1.0, April 2026

This template is provided to assist local jurisdictions with the implementation of adopted reach codes. It is not intended to provide guidance on the development of a reach code ordinance. Anyone developing a reach code ordinance should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ. This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose. You agree that your use of the template is without any recourse whatsoever to the developers of this document.

This document is intended as a compliance tool for typical 2025 local reach codes.  Modify it as needed to suit local requirements (especially blue italicized text).

# Scope

This checklist includes requirements for additions and replacements of single zone rooftop packaged HVAC systems with a capacity of 20 tons or less [10 tons or less in certain climate zones] in certain existing non-residential buildings.

# Instructions

- Make modifications following instructions and options in blue text. DELETE ALL BLUE TEXT BEFORE PUBLISHING

- Delete sections that do not apply, renumber sections as needed and edit requirements to align with local ordinance.

- Check all numbering and internal references after editing.

- Delete the cover page and this page.

This form is required for non-residential projects that include replacement of a single zone packaged rooftop HVAC system with a capacity of [240,000 Btu/hr or less or 120,000 Btu/hr or less]

These building standards have been established to ensure that construction in [jurisdiction] is healthier for occupants, has limited impact on the environment, reduces demand for energy, and results in cost savings from building operation over the life of the building. This checklist is intended to help applicants understand the process and specific local requirements that apply to their project.

For more information, please visit [jurisdiction website or other resource]

PROJECT PROCESS

- Project Design

It is important for project owners, architects, engineers, and designers to understand the applicable state and local building requirements prior to project design. Early consideration of these standards allows for design of buildings and systems that are compliant, energy efficient, and cost effective, and minimizes back and forth when applying for the project permit.

- Planning application (If required)

If your project is subject to planning review, be prepared to identify in your planning application which compliance methods you’ve selected and how you plan to meet the requirements. If you anticipate difficulties meeting the requirements, these concerns and any requests for exemptions should be identified in your planning application.

- Initial Building Permit Submittal

Include the following on your plans as part of your initial application for a building permit:

- Completed Local Building Decarbonization Checklist

- Title 24 Part 6 documentation demonstrating compliance with all State requirements

This form is required for non-residential projects that include a replacement single zone packaged rooftop HVAC system with a capacity of [240,000 Btu/hr or less or 120,000 Btu/hr or less]

PROJECT ADDRESS:______________________________________________________________

APN:___________________ APPLICANT NAME:________________________________________

- Scope of Requirements

Complete this form if the project scope includes a replacement single zone packaged rooftop HVAC system with direct expansion cooling with a capacity of [240,000 Btu/hr or less or 120,000 Btu/hr or less] serving any of the following occupancies: financial institution, grocery, library, office, school, or retail.  Units less than 65,000 Btu/hr are subject to the California Energy Code, Section 141.0(b)2Cii. Local requirements extend to units up to [240,000 Btu/hr or 120,000 Btu/hr]. These requirements are specified in [specify local code section].

2.	Single Zone Packaged Rooftop HVAC System Replacement

Complete either A, B, or C below. All Section references are to the California Energy Code, as amended.

- Projects with Replacement Systems with Heat Pumps Only

All replacement units include a heat pump that meets the requirements of Section 110.2.

B.	Projects with Replacement Systems other than Heat Pumps

Check all that apply to the project and complete Table 1.

The project includes a replacement unit(s) with a single zone air conditioner less than 65,000 Btu/hr that meets the requirements of Section 110.2 and Table 141.0-E-1.

The project includes a replacement unit(s) with a single zone air conditioner between 65,000 and [120,000 Btu/hr or 240,000 Btu/hr] with a single zone air conditioner that meets the requirements of Sections 110.2 and 141.0(b)2.C, has a heat recovery ventilation system that meets the requirements of Section 140.4(q) [,and has demand control ventilation that meets the requirements of Section 120.1(d)3].

- The project includes a replacement unit(s) with a single zone air conditioner that is subject to exceptions to the requirements of Section 141.0(b)2.C, as amended.

- The project includes a replacement unit(s) with a single zone air conditioner that does not serve any of the following occupancies: financial institution, grocery, library, office, school, or retail.

C. Performance Approach

- The project meets the performance compliance requirements of Section 141.0(b)3. Attach documentation.

3.	Project Verification

This form has been completed by _________________(name) of ________________(company), the qualified [specify credentials based on local practice, e.g., architect, engineer, project manager] individual for the above listed project who verifies that it accurately represents the project plans. [modify based on local verification requirements]

________________________________			______________

Signature								Date

Table 1: List of Replacement Single Zone Package Units. Include all units up to [240,000/120,000] Btu/hr. Attach additional pages as needed.

| Unit Name | Sheet/ Schedule Ref. | Occupancy | Capacity (Btu/hr) | Heat Pump? (Yes/No) | Heat Recovery Ventilation? (Yes/No) | Demand Control Ventilation? (Yes/No) | Variable Speed Fan and Economizer? (Yes/No) | Exception No., if applicable | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Exceptions

Heat Pump Exceptions

1. Where the capacity of the existing main electrical service panel is insufficient to supply the electrical capacity of a heat pump and where the existing main electrical service panel is sufficient to supply a new or replacement air conditioner, as calculated according to the requirements of California Electrical Code Article 220. Documentation of electrical load calculations in accordance with Article 220 must be submitted to the enforcement agency prior to permitting for both the heat pump and proposed air conditioner.

2. Where a licensed structural engineer determines that the roof would need a structural upgrade to support the additional weight of an appropriately sized SZHP but would not need a structural upgrade to support an equivalent SZAC. (Does not apply to units less than 65,000 Btu/hr.)

Exceptions to Demand Control Ventilation

3. Demand controlled ventilation in Section 120.1(d)4 is not required for SZAC4 replacements for spaces with a design occupant density, or a maximum occupant load factor for egress purposes in the CBC, less than 17 people per 1,000 square feet (59 square feet or more per person).

4. Where space exhaust is greater than the design ventilation rate specified in Section 120.1(c)3 minus 0.2 cfm per square foot of conditioned area, demand control ventilation is not required.

5. Spaces that have processes or operations that generate dusts, fumes, mists, vapors or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines or areas designated for unvented food service preparation, daycare sickrooms, science labs, barber shops or beauty and nail salons shall not install demand control ventilation.

6. Spaces with an area of less than 150 square feet, or a design occupancy of less than 10 people as specified by Section 120.1(c)3, are not required to install demand control ventilation.